INHYDRO

POLYHOUSE AUTOMATION SYSTEM
FUNCTIONAL & CONTROL DOCUMENT

Project: ITC Farm, Madhya Pradesh
Prepared by: Integrated Hydroponics India Pvt. Ltd. (INHYDRO)
Document Type: Automation Architecture, Functional Logic & HMI Specification
Revision: 02 | Date: 04 September 2026

# 1. Purpose of the Document

This document defines the proposed automation system for six polyhouses at the ITC Farm, Madhya Pradesh. It describes the field instrumentation, controller architecture, electrical interface, automatic/manual operation, irrigation/fogging logic, air circulation fan operation, HMI screens, cloud data communication, alarms and basic fail-safe philosophy.

# 2. Project Scope

| Polyhouse | Temperature/RH | CO₂ | PAR | DLI | ACF | Sprinkler | Fogger |
| --- | --- | --- | --- | --- | --- | --- | --- |
| PH-01 | Yes | Yes | Yes | Calculated | 24 | Yes | Yes |
| PH-02 | Yes | Yes | Yes | Calculated | 24 | Yes | Yes |
| PH-03 | Yes | Yes | Yes | Calculated | 24 | Yes | Yes |
| PH-04 | Yes | Yes | Yes | Calculated | 24 | Yes | Yes |
| PH-05 | Yes | Yes | Yes | Calculated | 24 | Yes | Yes |
| PH-06 | Yes | No | No | No | No | No | No |

Total: 6 polyhouses; environmental sensing in all six; CO₂ and PAR sensing in five; 120 ACFs across PH-01 to PH-05; five sprinkler solenoid valves; five fogger solenoid valves; and one common water pump/motor serving the sprinkler and fogger circuits.

# 3. Proposed Automation Architecture

The system will use a central industrial computing/control unit based on the proposed Raxda platform, Waveshare Modbus RTU relay modules, a USB hub, contactors/motor starters and a Waveshare HMI. Field sensors will communicate to the controller using suitable RS485/Modbus interfaces where applicable. The controller will execute the control logic, display live values on the HMI and publish operating data to the cloud.

Important electrical principle: the Waveshare Modbus relay outputs shall be used as control signals to interposing relays/contactors or suitable interface devices. Motors, pumps and groups of fans shall not be connected directly to low-power relay contacts unless the selected relay rating and protection are specifically verified.

# 4. System Block Diagram – Functional View

# 5. Hardware Architecture

| Component | Proposed Use | Qty / Requirement |
| --- | --- | --- |
| Raxda controller/computing platform | Central control, data processing, Modbus communication, cloud gateway | 1 central unit |
| Waveshare Modbus RTU Relay 32-Channel | Digital output control for contactors, solenoids and grouped devices | 1 × 32-channel modules, subject to final I/O allocation |
| USB Hub | Expansion for USB RS485/serial interfaces and peripherals | 2 or as required |
| Waveshare HMI | Local monitoring, setpoints, manual commands, schedules and alarms | 1 central HMI |
| Contactors / Motor Starters | Switching of pump and ACF power circuits | As per electrical load |
| Temperature + RH sensors | Environmental measurement | 6 |
| CO₂ sensors | CO₂ measurement | 5 |
| PAR sensors | PAR/PPFD measurement | 5 |
| Electrical Auto/Manual Panel | Local electrical mode selection and maintenance operation | 2 |
| Protection devices | MCB/MCCB, overload, control fuses, E-stop/interlocks as applicable | As per final electrical design |

# 6. I/O Philosophy and Relay Allocation

The ACFs are grouped by polyhouse. One relay output is assigned to each polyhouse ACF group, and that relay drives the corresponding contactor. The contactor then supplies power to all 24 ACFs in that polyhouse. The primary digital output requirement is 5 ACF group commands + 5 sprinkler solenoid commands + 5 fogger solenoid commands + 1 common pump command .n

| Output Group | Quantity | Control Method |
| --- | --- | --- |
| ACF PH-01 | 24 ACFs (grouped) | 1 relay → contactor → 24 ACFs |
| ACF PH-02 | 24 ACFs (grouped) | 1 relay → contactor → 24 ACFs |
| ACF PH-03 | 24 ACFs (grouped) | 1 relay → contactor → 24 ACFs |
| ACF PH-04 | 24 ACFs (grouped) | 1 relay → contactor → 24 ACFs |
| ACF PH-05 | 24 ACFs (grouped) | 1 relay → contactor → 24 ACFs |
| Sprinkler solenoid | 5 | One valve per polyhouse |
| Fogger solenoid | 5 | One valve per polyhouse |
| Common pump/motor | 1 | Contactor/motor starter |

# 7. Sensor Monitoring

The HMI shall display the current value, engineering unit, sensor status and communication status for every monitored parameter. The controller shall periodically poll the sensors and timestamp the received data before sending it to the cloud.

| Parameter | PH-01 to PH-05 | PH-06 | HMI Display | Cloud |
| --- | --- | --- | --- | --- |
| Temperature | Yes | Yes | Live + trend | Yes |
| Relative Humidity | Yes | Yes | Live + trend | Yes |
| CO₂ | Yes | No | Live + trend | Yes |
| PAR / PPFD | Yes | No | Live + trend | Yes |
| DLI | Calculated from PAR | No | Daily value + reset/status | Yes |

# 8. DLI Calculation

For each of PH-01 to PH-05, DLI will be calculated from the PAR/PPFD reading integrated over the photoperiod. If PPFD is available in µmol/m²/s, the controller can calculate daily photon integral as: DLI (mol/m²/day) = Σ[PPFD × elapsed seconds] / 1,000,000. For a constant PPFD, DLI = PPFD × photoperiod_seconds / 1,000,000. The displayed DLI should be identified as a calculated value unless the selected PAR instrument/controller provides an independent DLI output.

# 9. Automatic Control Philosophy

## 9.1 Setpoint Configuration

The client/operator shall be able to enter separate temperature and RH setpoints for each of PH-01 to PH-05. The recommended implementation uses ON and OFF thresholds (hysteresis) rather than a single threshold to prevent rapid relay cycling. Example: Fogger ON when temperature is above the configured high limit and/or RH is below the configured low limit; Fogger OFF after temperature/RH returns to the configured recovery limits. Exact default values shall be finalized with the agronomy/ITC team.

## 9.2 Fogger Control

When a polyhouse requires fogging, the controller first verifies that the common pump is permitted to run, then opens the selected polyhouse fogger solenoid and starts the common pump. The pump remains ON while at least one fogger demand is active. When no fogger demand remains, the relevant solenoid(s) close and the pump stops after an optional configurable post-run delay.

## 9.3 Sprinkler Control

Sprinkler operation shall be controlled from configurable environmental conditions and/or an operator-defined schedule. When a sprinkler demand is generated for a polyhouse, its sprinkler solenoid is opened and the common pump is started. The pump shall remain ON as long as one or more sprinkler/fogger zones require water. The controller shall prevent unnecessary pump starts/stops by applying a minimum ON/OFF time or zone sequencing where required.

## 9.4 Shared Pump Interlock

Because one common motor/pump serves five polyhouses, the control system shall use a shared-pump arbitration routine. Multiple zones may request water simultaneously, but the final hydraulic arrangement must be verified. If the pump cannot safely supply multiple zones at once, the controller shall queue requests and operate zones sequentially. The HMI should show the active zone and pending demand.

## 9.5 ACF Control

Each of PH-01 to PH-05 has 24 ACFs. The ACFs can be operated in automatic mode based on the configured environmental logic and/or cyclic timer. The system should support configurable ON/OFF thresholds, minimum run time, minimum rest time and cyclic operation. The exact fan grouping shall be finalized according to the electrical load and airflow design.

# 10. Auto / Manual Electrical Panel

A separate electrical panel shall provide Auto and Manual operation. In AUTO, the controller has authority to operate the field devices according to programmed logic. In MANUAL, authorized operators can command selected outputs from the electrical panel/HMI for testing and maintenance, subject to hardwired safety interlocks.

| Mode | Function |
| --- | --- |
| AUTO | Controller/HMI logic operates ACFs, solenoids and common pump. |
| MANUAL | Operator can test selected devices independently where electrically safe. |
| Emergency / Trip | Pump/fan operation is inhibited by relevant hardwired protection/trip. |
| Sensor Fault | Affected automatic function is placed into defined safe state and alarm is generated. |

# 11. HMI Screen Structure

The Waveshare HMI shall provide the following screens. Navigation shall be simple enough for farm operators while retaining configuration access for authorized users.

| Screen | Functionality |
| --- | --- |
| Screen 01 – Login / User Access | User login; operator/maintenance/admin levels; basic access control. |
| Screen 02 – Main Dashboard | Six polyhouses shown as tiles. Temperature, RH, CO₂, PAR and DLI where available; Auto/Manual status; pump status; active alarms. |
| Screen 03 – Polyhouse Overview | Select PH-01 to PH-06. Show all sensors, device states, setpoints, mode and communication health. |
| Screen 04 – PH-01 Detailed Control | Live Temp/RH/CO₂/PAR/DLI; fogger demand/state; sprinkler state; ACF states; setpoints; Auto/Manual status. |
| Screen 05 – PH-02 Detailed Control | Same functions as PH-01. |
| Screen 06 – PH-03 Detailed Control | Same functions as PH-01. |
| Screen 07 – PH-04 Detailed Control | Same functions as PH-01. |
| Screen 08 – PH-05 Detailed Control | Same functions as PH-01. |
| Screen 09 – PH-06 Detailed Monitoring | Temperature and RH only; no ACF, fogger, sprinkler or CO₂/PAR controls. |
| Screen 10 – Setpoint Configuration | Temperature high/low, RH high/low, fogging thresholds, sprinkler thresholds, hysteresis, minimum run/rest time. |
| Screen 11 – ACF Schedule / Cycle Timer | Fan ON duration, OFF duration, schedule windows and enable/disable per polyhouse. |
| Screen 12 – Irrigation / Fogging Schedule | Zone selection, start time, duration, repeat/cyclic operation and enable/disable. |
| Screen 13 – Manual Control | Authorized manual commands for ACF groups, sprinkler solenoids, fogger solenoids and pump, with safety interlocks. |
| Screen 14 – Trends | Temperature, RH, CO₂, PAR and DLI historical trends by polyhouse. |
| Screen 15 – Alarm History | Active/acknowledged alarms, timestamp, polyhouse, device and event description. |
| Screen 16 – Communication / Device Health | Sensor online/offline, Modbus status, relay status, HMI-controller link, cloud connectivity. |
| Screen 17 – System Settings | Date/time, units, sampling interval, cloud settings/status, user access and maintenance parameters. |

# 12. Recommended Main Dashboard Layout

The main dashboard should use six polyhouse tiles. Each tile shall display the most important live environmental values and a simple status indication. PH-01 to PH-05 should display Temp, RH, CO₂, PAR and DLI. PH-06 should display Temp and RH only. A common footer should show Pump status, system mode, cloud status and active alarm count.

Example tile:
PH-01 | TEMP: -- °C | RH: -- % | CO₂: -- ppm | PAR: -- µmol/m²/s | DLI: -- mol/m²/day
ACF: 24/24 | Sprinkler: OFF | Fogger: OFF | Mode: AUTO

# 13. Automatic Sequence Example

Example sequence for PH-02:
1. Controller reads PH-02 temperature and RH.
2. Temperature/RH are compared with configured setpoints.
3. If fogging demand becomes TRUE, PH-02 fogger solenoid opens.
4. Controller checks whether the common pump is already running. If not, pump contactor is energized.
5. PH-02 fogging continues until the configured OFF/recovery condition is reached or the maximum run timer expires.
6. Solenoid closes. If no other zone requires water, pump stops.
7. The event, start time, stop time and operating state are logged and sent to the cloud.
8. If a sensor fails, the controller raises an alarm and applies the configured safe-state strategy.

# 14. Priority / Arbitration Logic

| Priority | Condition | Action |
| --- | --- | --- |
| 1 | Emergency stop / electrical trip | Immediately inhibit affected outputs. |
| 2 | Pump protection / overload | Stop pump; close water solenoids; raise alarm. |
| 3 | Manual command | Allow authorized manual operation subject to safety interlocks. |
| 4 | Automatic environmental demand | Operate affected zone according to setpoints. |
| 5 | Scheduled/cyclic operation | Operate according to stored schedule when no higher priority condition overrides it. |
| 6 | Normal monitoring | Continue sensor acquisition, DLI calculation and cloud transmission. |

# 15. Alarm & Fault Management

| Alarm | Detection | Recommended Response |
| --- | --- | --- |
| Temperature sensor fault | No valid reading / communication timeout | Alarm; affected auto loop enters safe state. |
| RH sensor fault | No valid reading / communication timeout | Alarm; affected humidity loop enters safe state. |
| CO₂ sensor fault | PH-01…PH-05 invalid data | Alarm; CO₂ displayed as unavailable. |
| PAR sensor fault | PH-01…PH-05 invalid data | Alarm; DLI calculation marked invalid/incomplete. |
| Modbus communication fault | Repeated timeout/CRC/invalid response | Alarm and retry; preserve last known status only for diagnostics. |
| Pump overload/trip | Auxiliary contact / protection feedback | Stop water demand; close relevant valves; alarm. |
| Cloud communication loss | Heartbeat timeout | Local automation continues; data is buffered if supported and syncs after recovery. |
| ACF overload/trip | Protection feedback if provided | Alarm affected circuit; other circuits continue if safe. |

Rh alarm

# 16. Cloud Data Architecture

The controller shall act as the local data gateway. Sensor and equipment data shall be published to the cloud at a configurable interval. The cloud platform should retain historical values for analytics and visualization.

| Data Category | Parameters |
| --- | --- |
| Environment | Temperature, RH, CO₂, PAR/PPFD, DLI |
| Equipment | ACF ON/OFF, sprinkler valve state, fogger valve state, common pump state |
| Control | Setpoints, mode, schedule status, active demand |
| Events | Start/stop events, manual commands, alarms, trips |
| Health | Sensor communication, Modbus status, controller status, cloud connectivity |

Recommended cloud reporting: live dashboard + historical trends + daily summary + alarm/event history. The exact cloud protocol/API shall be finalized based on the selected ITC/cloud platform.

# 17. Data Logging & Sampling

A practical initial configuration is to acquire sensor values every 5–10 seconds for control, while publishing summarized data to the cloud every 30–60 seconds. The control loop and cloud publishing interval should remain independently configurable. High-frequency raw data may be retained locally or transmitted only where required.

# 18. Fail-Safe & Reliability Philosophy

The automation software shall not be the sole safety layer for electrically hazardous equipment. Motor overloads, short-circuit protection, emergency stop and other required electrical protections shall be hardwired in the electrical panel. Software interlocks shall supplement, not replace, these protections. On controller reboot, outputs shall initialize to a safe state and then resume automatic operation after sensor communication and safety conditions are verified.

# 19. Recommended Control Parameters

| Parameter | Configuration |
| --- | --- |
| Temperature High Setpoint | Per polyhouse, operator configurable |
| Temperature Recovery / Low Setpoint | Per polyhouse, operator configurable |
| RH High Setpoint | Per polyhouse, operator configurable |
| RH Recovery / Low Setpoint | Per polyhouse, operator configurable |
| Fogger minimum ON time | Configurable |
| Fogger minimum OFF time | Configurable |
| Sprinkler duration | Configurable |
| Sprinkler cyclic interval | Configurable |
| ACF cyclic ON time | Configurable |
| ACF cyclic OFF time | Configurable |
| Pump start delay | Configurable |
| Pump stop/post-run delay | Configurable |
| Sensor timeout | Configurable |
| Cloud publishing interval | Configurable |

The final numerical setpoints should be approved by the ITC agronomy/operations team for the specific crops and polyhouse environmental strategy. The automation design should not hard-code crop-independent temperature/RH values without that approval.

# 20. Operating Modes

| Mode | Description |
| --- | --- |
| AUTO | All configured automatic logic is active. |
| MANUAL | Operator can operate selected equipment for testing/maintenance. |
| SCHEDULE | Time-based programs operate within enabled schedule windows. |
| CYCLIC | ACF and/or irrigation can run according to ON/OFF cycle timers. |
| FAULT | Affected equipment is inhibited according to fault logic and alarm is generated. |

# 21. Commissioning & Testing

| Test Stage | Verification |
| --- | --- |
| Sensor test | Verify temperature/RH/CO₂/PAR readings against reference instruments where applicable. |
| Modbus test | Verify address, baud rate, parity, response and communication stability. |
| Relay test | Verify every output activates the intended contactor/valve circuit. |
| ACF test | Verify all 24 ACFs in PH-01…PH-05 individually/group-wise as designed. |
| Valve test | Verify each sprinkler and fogger solenoid. |
| Pump test | Verify start/stop, overload protection and pump feedback. |
| Auto logic test | Simulate setpoint conditions and verify automatic response. |
| Manual test | Verify manual commands and safety interlocks. |
| Cloud test | Verify live data, timestamps, historical trends and alarms. |
| Power recovery test | Verify safe restart and return to AUTO after controller reboot. |

# 22. Final Functional Summary

The proposed INHYDRO automation system will provide centralized monitoring and control for all six polyhouses. PH-01 to PH-05 will have temperature, RH, CO₂ and PAR monitoring with calculated DLI, 24 ACFs, sprinkler and fogger solenoids, and access to a common water pump. PH-06 will be a monitoring-only polyhouse with temperature and RH. The Waveshare HMI will provide live monitoring, setpoint entry, schedules, cyclic timers, manual control, trends, alarms and system diagnostics. The Raxda controller will execute the local automation logic and communicate field devices through Waveshare Modbus relay modules and suitable electrical interface hardware. Data from all monitored parameters and equipment states will be shared with the cloud for remote monitoring and analytics.

# 23. Engineering Notes / Items to Freeze Before Panel Manufacturing

Confirm exact Raxda controller model, operating system and available communication ports.

Confirm exact Waveshare HMI model and communication protocol.

Confirm all sensor models, output formats, Modbus registers, addresses and power supplies.

Confirm CO₂ and PAR sensor installation locations and calibration requirements.

Confirm ACF motor rating and whether 120 fans are individually switched or grouped.

Confirm common pump/motor rating, starter type and overload protection.

Confirm solenoid valve voltage and current.

Confirm whether sprinkler and fogger can operate simultaneously in different zones based on hydraulic capacity.

Finalize Auto/Manual philosophy and hardwired interlocks with the electrical design.

Finalize numerical temperature/RH setpoints with the crop/agronomy team.

Finalize cloud platform, API/MQTT/HTTPS method, data retention and remote-access requirements.

Finalize cable schedule, panel I/O schedule, Modbus network topology, earthing and surge protection.

# 24. Proposed Deliverables by INHYDRO

Automation control architecture and electrical interface design.

HMI screen development and configuration.

PLC/industrial-controller application logic on the selected Raxda platform.

Modbus relay configuration and I/O mapping.

Sensor integration and calibration support.

Auto/manual control logic and safety interlocks.

Cloud data integration and dashboard data feed.

Alarm, event and trend functionality.

Factory/site testing and commissioning support.

Operator handover and basic system documentation.

# 20A. ACF Group Control Clarification

Each of PH-01 to PH-05 has 24 ACFs, but the 24 ACFs within a polyhouse are treated as one electrical control group. One digital relay output commands one contactor for that polyhouse. The contactor supplies the electrical power to the 24 ACFs. Thus, the automation system controls five ACF groups rather than 120 individually switched fans. Individual fan-level monitoring or control is not included in the base scope unless specifically added.

Base relay output calculation: ACF groups = 5; sprinkler solenoids = 5; fogger solenoids = 5; common pump = 1; total primary outputs = 16. One 32-channel Modbus relay provides 16 spare channels for future expansion, subject to final electrical design.

Note:-

- Alarm Notification

- Password

- Setpoint change notification

- Sensor error notification

- Give 5 cyclic timer

| Condition | Fogger | Sprinkler | Pump | ACF | ALARM |
| --- | --- | --- | --- | --- | --- |
| High temp + normal RH | ON | ON | ON | ON |  |
| High temp + high RH | OFF | ON | ON | ON | YES |
| Normal temp +low rh | ON | OFF | ON | ON |  |
| Normal temp + normal RH | OFF | OFF | OFF | OFF |  |
| Low RH | ON* | OFF | ON | ON |  |
| High RH | OFF | OFF | OFF | Depends on ventilation requirement | YES |
| temp low ,humidity low | ON | OFF | ON | OFF |  |

# REVISED SYSTEM BLOCK DIAGRAM – FINAL ARCHITECTURE

FIELD SENSORS – 6 POLYHOUSES

PH-01  [Temp/RH] [CO₂] [PAR] ─┐
PH-02  [Temp/RH] [CO₂] [PAR] ─┤
PH-03  [Temp/RH] [CO₂] [PAR] ─┤
PH-04  [Temp/RH] [CO₂] [PAR] ─┤
PH-05  [Temp/RH] [CO₂] [PAR] ─┤
PH-06  [Temp/RH] ─────────────┘
                 │
                 │ RS485 / USB / Ethernet
                 ▼
        ┌──────────────────────────────┐
        │       RAXDA CONTROLLER       │
        │ • Sensor acquisition          │
        │ • Temp/RH control logic       │
        │ • Fogger / sprinkler logic    │
        │ • ACF cyclic timer            │
        │ • DLI calculation             │
        │ • Alarm & event management    │
        │ • Cloud communication         │
        └──────────────┬───────────────┘
                       │
              Modbus RTU / RS485
                       │
                       ▼
        ┌──────────────────────────────┐
        │ WAVESHARE 32-CH MODBUS RELAY │
        │      16 primary outputs       │
        │      16 spare outputs         │
        └───────┬─────────┬────────────┘
                │         │
       ┌────────┘         └───────────────┐
       ▼                                  ▼
 ACF GROUP CONTROL                  WATER CONTROL
 1 relay per polyhouse              5 sprinkler valves
       │                             5 fogger valves
       ▼                             1 common pump
 ┌───────────────┐                         │
 │  CONTACTORS   │                         │
 └───────┬───────┘                         │
         │                                  │
         ▼                                  ▼
 PH-01: 24 ACFs                     ┌───────────────┐
 PH-02: 24 ACFs                     │ CONTACTOR /   │
 PH-03: 24 ACFs                     │ MOTOR STARTER │
 PH-04: 24 ACFs                     └───────┬───────┘
 PH-05: 24 ACFs                             │
                                            ▼
                                      COMMON PUMP
                                            │
                         ┌──────────────────┴─────────────────┐
                         ▼                                    ▼
                 Sprinkler Solenoids                     Fogger Solenoids
                   PH-01 … PH-05                           PH-01 … PH-05

                     ┌───────────────────────────┐
                     │      WAVESHARE HMI        │
                     │ Live values • Setpoints   │
                     │ Auto/Manual • Timers      │
                     │ Trends • Alarms • Status  │
                     └─────────────┬─────────────┘
                                   │
                                   ▼
                            CLOUD / WEB APP

Final architecture note: The five sets of 24 ACFs are electrically grouped by polyhouse. One relay output commands one contactor for each polyhouse, and the contactor supplies the 24 ACFs. The relay module therefore does not require 120 ACF outputs.

# FINAL I/O SUMMARY

| Output Function | Quantity | Relay Outputs | Interface |
| --- | --- | --- | --- |
| ACF PH-01 to PH-05 | 24 ACFs × 5 | 5 | Relay → contactor → ACF group |
| Sprinkler solenoids | 5 | 5 | Relay → solenoid/interface |
| Fogger solenoids | 5 | 5 | Relay → solenoid/interface |
| Common pump | 1 | 1 | Relay → contactor/motor starter |
| Total primary outputs |  | 16 | One 32-channel module |
| Spare capacity |  | 16 | Available for future expansion |

# FINAL ACF CONTROL PRINCIPLE

Each polyhouse is treated as one ACF control zone. For example, PH-01 has 24 ACFs. When the PH-01 ACF command becomes ON, the Raxda energizes the corresponding Waveshare relay. That relay operates the PH-01 ACF contactor, which switches all 24 ACFs together. The same principle applies to PH-02, PH-03, PH-04 and PH-05. PH-06 has no ACF.

# FINAL WATER CONTROL PRINCIPLE

Each of PH-01 to PH-05 has one sprinkler solenoid and one fogger solenoid. The solenoid selects the required polyhouse water zone, while the single common pump supplies water. The Raxda determines pump demand from the active sprinkler/fogger requests. Where the hydraulic system cannot support simultaneous zones, the controller shall sequence the requests so only permitted zones operate at a time.

# FINAL HMI FUNCTIONAL STRUCTURE

| HMI Screen | Main Function |
| --- | --- |
| Dashboard | Six polyhouse tiles; live environmental values; equipment status; pump; alarms. |
| PH-01 to PH-05 | Temp, RH, CO₂, PAR, DLI, ACF group, sprinkler, fogger and setpoints. |
| PH-06 | Temperature and RH monitoring only. |
| Setpoints | Temperature/RH thresholds, hysteresis, fogger/sprinkler parameters. |
| ACF Timer | Auto operation, cyclic ON/OFF time and enable/disable. |
| Irrigation/Fogger Timer | Schedule, duration, repeat/cyclic operation. |
| Manual Control | Authorized manual operation with safety interlocks. |
| Trends | Historical Temp, RH, CO₂, PAR and DLI. |
| Alarms | Sensor, Modbus, pump, ACF and cloud communication faults. |
| System Health | Controller, HMI, Modbus, sensors and cloud status. |